Disinfection Plan

Newly Constructed Potable Water Mains

Tablet/Granule Method

(Up to 16” Diameter)

Austin Water Utility

Project Name: __________________________________________

SP # or CIP ID __________________________________________

Engineering Firm ________________________________________

Engineer of Record _______________________________________

Contractor ______________________________________________

Disinfection Contractor ___________________________________

City of Austin Inspector ___________________________________

Prepared by with email_______________________________________

Preparer’s Telephone ______________________________________

Estimated date of flushing___________________________________

With the submittal of this plan, include a copy of the waterline sheets.  Make sure the sheets include the WL stationing and show callouts for appurtenances.  Please include all backup documentation to support the chlorination and dechlorination chemicals.

If the total length of the connection from the end of the new main to the existing main is equal to or less than 20 ft, as an optional procedure, the new pipe, fittings, and valve(s) required for the connection may be spray-disinfected or swabbed with a minimum 1 percent solution of chlorine just prior to being installed.  If you plan on using this procedure, just email Eric Langhout at eric.langhout@austintexas.gov, with Pipeline Engineering, the waterline sheet for approval.  You will not need to fill out this form.

Project Description (LF, pipe diameter, pipe capacity)

_______LF      ____  Inch Waterline     Capacity  ___________gallons

_______LF      ____  Inch Waterline     Capacity  ___________gallons

_______LF      ____  Inch Waterline     Capacity  ___________gallons

_______LF      ____  Inch Waterline     Capacity  ___________gallons

_______LF      ____  Inch Waterline     Capacity  ___________gallons

_______LF      ____  Inch Waterline     Capacity  ___________gallons

_______LF      ____  Inch Waterline     Capacity  ___________gallons

_______LF      ____  Inch Waterline     Capacity  ___________gallons

Section 1.  Preparation

Section 1.A.  Preventative and Corrective Measures during Construction

Proper precautions shall be taken to assure the pipe remains clean and dry during construction including but not limited to those preventative and corrective measures indicated in section 4.8 of AWWA C651-14.

Section 1.B.  Measurement of Water used in Disinfection Process

All water used in the process shall be measured.  Measurement shall be accomplished by filling out the attached “Volume of Water used for Flushing” spreadsheet.  Payment for water use will not be required by the construction contractor.

Section 1.C.  Water Supply

Water shall be supplied through (Only 1 connection of the new waterline system to the existing main is allowed.  Submit one plan per connection to main):

_______One Connection of new main to existing main at Station ________________

(Valve isolating new main from existing potable water system shall be tagged to prevent unintentional release of the elevated chlorine residual to the system.)

OR

_______Temporary flushing/testing connection by connecting temporary plug on new main at no more than 20’ from the proposed tie-in point to the existing main at Sta _______ to existing FH # ____________  equipped with cross connection control device.

Section 2.  Discharge

Discharge shall be within 20 feet of end of new main at the following location(s)

_____Existing new fire hydrant Sta ____________

_____Existing new Service  Sta __________  Size _______

_____Temporary combination blowoff and sampling tap at Sta _________

Contractor’s Selected Method (circle one)       Tablet   Granule

Section 3.A. Calcium Hypochlorite

Calcium Hypochlorite shall conform to ANSI/AWWA B300 and NSF 61 and must contain approximately 65 percent chlorine by weight and must be stored in a cool, dry, dark environment to minimize deterioration.  DO NOT USE calcium hypochlorite intended for swimming pool disinfection, as this material has been sequestered and is extremely difficult to eliminate from the pipe after the desired contact time has been achieved.

WARNING:  Calcium hypochlorite must not be used on solvent-welded plastic or on screwed-joint steel pipe because of the danger of fire or explosion.

Brand/Manufacturer __________________________

Percent Available Chlorine  _____________________

(Submit MSDS)

Section 3.B. Tablet Method

Calcium Hypochlorite Tablets

5-g calcium hypochlorite tablets shall be placed in each section of pipe (number of tablets per section shall comply with following table).

Main size _____ length of sections ______

Length of Pipe Section (ft)

Pipe Diameter (inches)                                       18                     20

Number of 5-g Calcium Hypochlorite Tablets

*3.5 g available Chlorine per tablet (70%)

4                                                                           1                        1

6                                                                           1                        1

8                                                                           2                        2

12                                                                         4                        4

16                                                                         6                        7

Additionally, one tablet shall be placed in each hydrant, hydrant branch, and other appurtenance as indicated below:

Station                                   Description

________________________________________

________________________________________

_________________________________________

Tablets shall be attached by a food-grade adhesive.  Adhesive shall be only on the broadside of the tablet attached to the surface of the pipe.  The tablets shall be attached to the top of the main.  If the tablets are attached before the pipe section is placed in the trench, their position shall be marked on the section to indicate that the pipe has been installed with the tablets at the top.

Section 3.C. Granule Method

Calcium Hypochlorite Granules shall be placed in the main during construction at the following stations to include the upstream end of first section of pipe, upstream end of each branch and at 500’ intervals.  Quantity to be in accordance with the following table:

Pipe Diameter (d) (inches)                                  Calcium Hypochlorite Granules (ounces)

1.5                                                                          0.24

2                                                                             0.4

- 1.7

6                                                                             3.8

8                                                                             6.7

12                                                                           15.1

Over 12”                                                               * D X D X 15.1

16                                                                           26.8

*D= inside pipe diameter in feet

Example for 8” WL at 1000 lf: (1000/ 500) x 6.7

Station numbers for placement:

Station #                            Description                        Ounces of Granules

_______________________________________________________________
_______________________________________________________________
_______________________________________________________________
_______________________________________________________________
_______________________________________________________________

Section 4.  Pre- Flushing of Source Water

The source of potable water used for disinfection and pressure testing shall be flushed prior to its use to ensure that contaminants or debris are not introduced into the new pipe.

Section 5. Filling and Contact

When installation has been completed, the main shall be filled with water at a rate to ensure that the water within the main will flow at a velocity no greater than 1 ft/sec to avoid washing out the chlorine granules or tablets.  Precautions shall be taken to ensure air pockets are eliminated.    The chlorinated water shall be retained in the pipe for at least 24 hours.  If the water temperature is less than 41 degrees F, the water shall remain in the pipe for at least 48 hours.  A detectable free chlorine residual should be found at each sampling point after the retention period.  Minimum water required for initial fill equal the capacity of all new pipe.  Though not required, the City recommends using a meter to determine the flow rate.

Flow rate for 1fps velocity =                 gpm

Capacity of new pipe =                          gallons

Time required to fill =                            minutes

Section 6.   Disinfection of Appurtenances

Disinfection of appurtenances shall occur while new main is heavily chlorinated by operating all valves, hydrants, and service connections to ensure contact with the chlorinated water.

Appurtenances

Sta                          Description                 Operated (Check when operated)

________________________________________________________________________

________________________________________________________________________

________________________________________________________________________________________________________________________________________________

Section 7.  Final Flushing

After the applicable retention period, heavily chlorinated water should not remain in prolonged contact with pipe.  Chlorinated water shall be flushed from the main, fittings, valves, and branches until chlorine measurements show that the concentration in the water leaving the main is no higher than that generally prevailing in the distribution system or that is acceptable for domestic use.  (Typically 0.50 – 2.0 mg/L)  A minimum of one times the volume of water in the new pipe shall be flushed.  Flushing velocity of 3.0 fps is recommended.  Though not required, the City recommends using a meter to determine the flow rate.

Flow rate for final flushing  = ______________  gpm  _____________ fps

Amount of discharge water anticipated for final flushing =  ___________gallons

Estimated time for final flushing =  ________________  minutes

Section 8.  Dechlorinating and Disposing of Chlorinated Water

All heavily chlorinated water discharged during this procedure shall be dechlorinated and disposed of properly.

Section 8.A Dechlorination Chemical

Dechlorination chemicals of food grade quality shall be used to dechlorinate all water discharged from the system adequately to result in no detectable chlorine residual when measured by an appropriate low level chlorine test kit before the water reaches the curb inlet, wastewater manhole, or receiving streams or wetlands.

Amounts of chemicals required to neutralize various residual chlorine concentrations in 100,000 gallons of water. Table below from AWWA C655-09 – User should confirm required dosage with chemical supplier.  Water leaving the new main shall receive a dose of the dechlorination chemical fed at a constant rate assuming the line will have 25 mg/L (ppm) of residual chlorine concentration.  The residual chlorine concentration in the water leaving the main shall be measured at regular intervals using appropriate chlorine test kits to insure it does not exceed 1 mg/L.

Residual               Calcium             Sodium             Ascorbic        Sodium        Sodium

Chlorine            Thiosulfate        Thiosulfate             Acid           Bisulfite        Sulfite

Concentration    (CaS2O3)    (Na2S2O3-5H20)    (C6O8H6)    (NaHSO3)    (Na2SO3)

Mg/L                       gal                        lb                       lb                  lb                 lb

1                             0.34                      1.2                     2.1                1.2               1.4

2                             0.67                      2.4                     4.2                2.5               2.9

10                           3.36                    12.0                   20.9              12.5             14.6

25                           8.4                      30.0                   52.0              31.3             36.5

50                         16.8                      60.0                 104.0              62.6             73.0

Chlorine Concentration prior to Dechlor   __________ mg/L

Pipe Capacity   ____________ gallons

Type of Chemical ____________________________

Brand/Manufacturer  ________________________  (submit MSDS)

Chemical quantity required _________________ lb

Example for Calcium Thiosulfate for 1000 gallons (1000 / 100,000) x 8.4

If multiple discharge locations are being used, please provide a sequence of dechlorination that describes when valves and end of line locations will be opened and closed so that all pipe sections received the required amount of chlorine.

Sequence (if applicable)

________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Section 8.B. Discharge/Disposal

Optional discharge methods are indicated below in order of preference:

  - Beneficial reuse – Discharge to a water truck and used for beneficial use such as irrigation, watering for dust control, or other acceptable beneficial construction use.  MAY NOT be used as potable water for consumption.

  - Storm Sewer/Retention Pond – May be transported by hose to storm sewer inlet which discharges to a retention pond or holding pond approved by AWU.  An air gap shall be maintained between the discharge end of the hose and the inlet.

  - Wastewater Manhole – May be transported by hose to wastewater manhole subject to approval of Austin Water Utility.  An air gap must be maintained between the discharge end of the hose and the manhole.

---AIR GAP REQUIRED AT DISCHARGE POINT FOR ALL METHODS.-----

(Contractor shall check selected method.)

_______   Beneficial reuse -  Dechlorinated water shall be loaded into a _________ gallon capacity water truck and conveyed to (describe location(s)) ________________________________________________________________________________________________________________________________________________                                        for (describe use)  ________________________________________________________________________________________________________________________________________________________________________________________________________________________

_________ Storm sewer disposal - Dechlorinated water shall be transported from discharge point at Sta __________ to storm sewer inlet at Sta _____________ via _________ LF fire hose.  Storm sewer discharges into water quality pond located at (describe)  ___________________________________________________________.

Total estimated gallons to be discharged from disinfection and flushing operation ___________ .  Flow rate into storm sewer inlet ___________ gpm.

For support with runoff issues, contact the 24-hour Pollution Hotline at 974-2550.

_______  Sanitary Sewer disposal.  Dechlorinated water shall be transported from  discharge point at Sta __________ to sanitary sewer manhole at Sta _____________ via _________ LF fire hose.

Total estimated gallons to be discharged from disinfection and flushing operation ___________ .  Flow rate into sanitary sewer manhole ___________ gpm.

Section 9.  Bacteriological Tests

After disinfection and final flushing such that typical system chlorine residuals are present, if the system operates with a residual, samples shall be collected per one of the two options.  Option A: Before approving a main for release, take an initial set of samples and resample again after a minimum of 16 hours using the sampling site procedures outlined.  Both sets of samples must pass for the main to be approved for release.  Option B: Before approving a main for release, let it sit for a minimum of 16 hours without any water use.  Then collect, using the sampling site procedures outlined and without flushing the main, two sets of samples a minimum of 15 minutes apart while the sampling taps are left running.  Both sets of samples must pass for the main to be approved for release.

- Sample Locations.  As a minimum, at least one set of samples shall be taken from the end of the line(s), from each branch, and at intervals not to exceed 1200 feet of the new main.  If there is reason to believe that trench water has entered the new main during construction or if, in the opinion of the purchaser, excessive quantities of dirt or debris have entered the main, the AWU representative may require samples be taken at intervals of approximately 200 feet.

Sample Locations (List by Station and Description)

________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

- Procedure - No hose shall be used in the collection of samples.  Use of a combination blowoff and sampling tap is recommended.  Samples shall be collected by City of Austin personnel in sterile bottles treated with sodium thiosulfate.

- Sample results – If initial samples produce acceptable laboratory results, a second set of samples will be taken 16 hours after the first sample.  CAUTION:  NO flushing shall be allowed between sampling except as needed to flush the sampling port.) If sample results from the lab indicate a measured HPC greater than 500 colony-forming units (cfu) per mL, flushing shall be resumed and another set up samples should be taken until no coliforms are present.

- Redisinfection – If two successive passing samples cannot be achieved, the new main may be reflushed and shall be resampled.  If these samples also fail to produce acceptable results, the main shall be rechlorinated by continuous feed method until satisfactory results are obtained – that being acceptable samples taken as described in Section 9.

Date/Time 1st Samples Collected ______________________  Pass/Fail

Date/Time 2nd Sample Collected  ______________________  Pass/Fail

Section 10.  Removal of Temporary Connections

After satisfactory bacteriological sample results have been received, all temporary connections installed for this procedure (temporary connections, temporary injection point, temporary flushing devices) must be appropriately cut and plugged at the water main.

Section 11. Final Connection to Existing Mains

After satisfactory bacteriological sample results have been received, permanent connections may be made to the active distribution system.  Sanitary construction practices must be followed during installation of the final connection to prohibit contamination of the new or existing water main.

Section 11.A.  Connection of pipe length less than or equal to 20 feet

New pipe, fittings, and valves required for the connection must be spray-disinfected or swabbed with a minimum of 1 percent solution of chlorine just prior to being installed.

Section 11.B. Connection of pipe greater than 20 feet

Pipe required for the connection must be set up above ground, disinfected, and bacteriological samples taken as described in Section 8.  After satisfactory bacteriological sample results have been received, the pipe can be used in connecting the new main to the active distribution system.  Between the time satisfactory sample results have been received and the time that the connection piping is installed, the ends of the pipe must be sealed with plastic wraps, watertight plugs, or caps.

Appendix

Table 1:  Velocity (fps) Conversion to Flow Rate (gpm)(Q=VA)

| Pipe size (in) | Velocity (fps) | Q (gpm) |
| --- | --- | --- |
| 1.5 | 1 | 6 |
| 1.5 | 3 | 17 |
| 2 | 1 | 10 |
| 2 | 3 | 29 |
| 4 | 1 | 39 |
| 4 | 3 | 118 |
| 6 | 1 | 88 |
| 6 | 3 | 264 |
| 8 | 1 | 157 |
| 8 | 3 | 470 |
| 10 | 1 | 245 |
| 10 | 3 | 734 |
| 12 | 1 | 352 |
| 12 | 3 | 1058 |
| 16 | 1 | 627 |
| 16 | 3 | 1880 |
| 24 | 1 | 1410 |
| 24 | 3 | 4230 |

Table 2:  Pipe Capacity (gallons)

| Pipe Dia | Area | Volume Per 100 LF | Capacity Per 100 lf |
| --- | --- | --- | --- |
| (in) | (sf) | (cf) | (gallons) |
| 1.5 | 0.012272 | 1.23 | 9 |
| 2 | 0.021817 | 2.18 | 16 |
| 4 | 0.087266 | 8.7 | 65 |
| 6 | 0.19625 | 20 | 147 |
| 8 | 0.348888889 | 35 | 261 |
| 10 | 0.545415391 | 55 | 408 |
| 12 | 0.785 | 79 | 587 |
| 16 | 1.395555556 | 140 | 1,044 |
| 24 | 3.14 | 314 | 2,349 |
| 30 | 4.9087385 | 491 | 3,672 |
| 36 | 7.06858 | 707 | 5,288 |
| 42 | 9.621127502 | 962 | 7,196 |
| 48 | 12.56637061 | 1,257 | 9,400 |
| 54 | 15.90431281 | 1,590 | 11,894 |
| 66 | 23.7582944 | 2,376 | 17,772 |